## Sheet1
DATE | BLDG | FLR | DLCC | BUS | Status
2007-05-17 | 3 | 1 | 31DA | AA | done Move PS AA-107 10' east & 14' south. Verify Group setting for DPSI AA-73,75
| 3 | 1 | 31DA | AB | Reconnect two short rows to Bus AB
| 3 | 1 | 31DA | AC | Reconnect Small Conf 3135 to Bus AC
| 3 | 1 | 31DA | AD | Reconnect three downlights to Bus AD
2007-05-10 | 3 | 1 | 31DA | AE | done Move PS AE-104 2' east and 2' north. Verify Group of DPSI FE-74.
2007-05-10 | 3 | 1 | 31DA | AF | done Move PS AF-100 12' east.
2007-05-10 | 3 | 1 | 31DA | AG | done Turn off temporary construction work lights in ceiling cavity.
2007-05-17 | 3 | 1 | 31DA | AH | done Move PS AH-101 2' east & 2' north. Had to enter correct group in one DS.
2007-05-17 | 3 | 1 | 31DB | BA | done Move OS7 BA-100 to northeast corner of Copy Rm 3105.
2007-05-10 | 3 | 1 | 31DB | BB | done Verify Group setting for DPSI BB-76 (#08).
2007-05-17 | 3 | 1 | 31DB | BC | done Had to enter correct group in three DS
2007-05-17 | 3 | 1 | 31DB | BD | done
2007-05-17 | 3 | 1 | 31DB | BE | done
| 3 | 1 | 31DB | BF | Reconnect three downlights to Bus AD
| 3 | 1 | 31DB | BG | spare to Main Elect Rm 3131B
2007-05-10 | 3 | 1 | 31DB | BH | done
2007-04-24 | 3 | 2 | 32DC | CA | done Verify group setting on DPSI CA-71 in Small Conf.
2007-04-24 | 3 | 2 | 32DC | CB | done Can not get full signal strength to CB-39 thru -42
2007-04-17 | 3 | 2 | 32DC | CC | done
2007-04-17 | 3 | 2 | 32DC | CD | done Verify Group setting of DPSI CD-70. RNM to set scenes in 3239
2007-04-17 | 3 | 2 | 32DC | CE | done Fix warpped housing between CE-28 and CE-32. Verify Group setting of DPSI CE-70 5/3/07 Had to readdress and reprogram CE-37.
2007-04-17 | 3 | 2 | 32DC | CF | done Move PS CF-100 10' east.
2007-04-24 | 3 | 2 | 32DC | CG | done
2007-04-24 | 3 | 2 | 32DC | CH | done Verify group setting on DPSI CH-85 in Med Conf. Move PS CH-107 away from uplight. Check lamp in CH-19. Install TP in 3210. RNM so set scenes in Team 3210
2007-04-24 | 3 | 2 | 32DD | DA | done Check lamp/ballast in DA-26 RNM changed Balcony from #06 to #12 & #13. RNM changed Hall 3215 from #04 to #14 & #15.
2007-04-17 | 3 | 2 | 32DD | DB | done OS are not installed but OS wires are pluged in DOSI therefore AUTO turn off. RNM so set scenes in Quiet3225A & Mothers 3225B.
2007-04-25 | 3 | 2 | 32DD | DC | almost done Install DS at doors near DC-6 and near DC-48 as shown on CEI drawing 32E-2.2.
2007-04-25 | 3 | 2 | 32DD | DD | almost done Fix DALI continuity to DD-30 thru 33.
2007-04-25 | 3 | 2 | 32DD | DE | done
2007-04-17 | 3 | 2 | 32DD | DF | done
2007-04-24 | 3 | 2 | 32DD | DG | done
2007-04-17 | 3 | 2 | 32DD | DH | done
| 3 | 2 | 32DE | EA
| 3 | 2 | 32DE | EB
| 3 | 2 | 32DE | EC
| 3 | 2 | 32DE | ED
| 3 | 2 | 32DE | EE
| 3 | 2 | 32DE | EF
| 3 | 2 | 32DE | EG
| 3 | 2 | 32DE | EH
2007-04-12 | 3 | 3 | 33DF | FA | done Had to enter correct Group in DS FA-73, 79, 82
2007-04-10 | 3 | 3 | 33DF | FB | done
2007-04-10 | 3 | 3 | 33DF | FC | done
2007-04-10 | 3 | 3 | 33DF | FD | done REPLACE lamp in FD-57. Had to enter correct Group in DS FD-73 & FD-75.
2007-04-11 | 3 | 3 | 33DF | FE | done Had to enter correct Group in DS FE-73.
2007-04-11 | 3 | 3 | 33DF | FF | done
2007-04-10 | 3 | 3 | 33DF | FG | done
2007-04-12 | 3 | 3 | 33DF | FH | done Install TP in 3310. RNM so set scenes in Team 3310
2007-04-12 | 3 | 3 | 33DG | GA | done Had to enter correct Group in DS GA-80, 82, 84.
2007-04-11 | 3 | 3 | 33DG | GB | done
2007-04-11 | 3 | 3 | 33DG | GC | done EC fixed DALI signal to GC-39. Had to enter correct Group in DS GC-73
2007-04-11 | 3 | 3 | 33DG | GD | done
2007-04-11 | 3 | 3 | 33DG | GE | done
2007-04-11 | 3 | 3 | 33DG | GF | done
2007-04-11 | 3 | 3 | 33DG | GG | done
2007-04-11 | 3 | 3 | 33DG | GH | done